## FY18 Filter Test
RECORD ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  |  | WATER FILTERS Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001050 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD C, in hallway adjacent to C102 | Left | High | WF-122017-001050 | 2017-12-26 | FT-FY18-122017-001050-A | <1 | FT-FY18-122017-001050-B | <1
WS- 001051 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD C, in hallway adjacent to C102 | Right | Low | WF-122017-001051 | 2017-12-26 | FT-FY18-122017-001051-A | <1 | FT-FY18-122017-001051-B | <1
WS- 001052 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD C, in hallway adjacent to C102 | Left | High | WF-122017-001052 | 2017-12-26 | FT-FY18-122017-001052-A | <1 | FT-FY18-122017-001052-B | <1
WS- 001053 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD C, in hallway adjacent to C102 | Right | Low | WF-122017-001053 | 2017-12-26 | FT-FY18-122017-001053-A | <1 | FT-FY18-122017-001053-B | <1
WS- 001054 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD A, in hallway adjacent to A109 | Left | High | WF-122017-001054 | 2017-12-26 | FT-FY18-122017-001054-A | <1 | FT-FY18-122017-001054-B | <1
WS- 001055 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD A, in hallway adjacent to A109 | Right | Low | WF-122017-001055 | 2017-12-26 | FT-FY18-122017-001055-A | <1 | FT-FY18-122017-001055-B | <1
WS- 001056 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD A, in hallway adjacent to A109 | Left | High | WF-122017-001056 | 2017-12-26 | FT-FY18-122017-001056-A | <1 | FT-FY18-122017-001056-B | <1
WS- 001057 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD A, in hallway adjacent to A109 | Right | Low | WF-122017-001057 | 2017-12-26 | FT-FY18-122017-001057-A | <1 | FT-FY18-122017-001057-B | <1
WS- 001058 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD B, in hallway adjacent to B107 | Left | High | WF-122017-001058 | 2017-12-26 | FT-FY18-122017-001058-A | <1 | FT-FY18-122017-001058-B | <1
WS- 001059 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD B, in hallway adjacent to B107 | Right | Low | WF-122017-001059 | 2017-12-26 | FT-FY18-122017-001059-A | <1 | FT-FY18-122017-001059-B | <1
WS- 001060 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD B, in hallway adjacent to B107 | Left | High | WF-122017-001060 | 2017-12-26 | FT-FY18-122017-001060-A | <1 | FT-FY18-122017-001060-B | <1
WS- 001061 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD B, in hallway adjacent to B107 | Right | Low | WF-122017-001061 | 2017-12-26 | FT-FY18-122017-001061-A | <1 | FT-FY18-122017-001061-B | <1
WS- 001062 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD D, in hallway adjacent to D109 | Left | High | WF-122017-001062 | 2017-12-26 | FT-FY18-122017-001062-A | <1 | FT-FY18-122017-001062-B | <1
WS- 001063 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD D, in hallway adjacent to D109 | Right | Low | WF-122017-001063 | 2017-12-26 | FT-FY18-122017-001063-A | <1 | FT-FY18-122017-001063-B | <1
WS- 001064 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD D, in hallway adjacent to D109 | Left | High | WF-122017-001064 | 2017-12-26 | FT-FY18-122017-001064-A | <1 | FT-FY18-122017-001064-B | <1
WS- 001065 | 2017-12-12 | 2018-12-12 | Ground Floor | Cooler | POD D, in hallway adjacent to D109 | Right | Low | WF-122017-001065 | 2017-12-26 | FT-FY18-122017-001065-A | <1 | FT-FY18-122017-001065-B | <1
WS- 001066 | 2017-12-18 | 2018-12-18 | Ground Floor | Health Suite | POD D, in Health Suite |  |  | WF-122017-001066 | 2017-12-26 | FT-FY18-122017-001066-A | <1 | FT-FY18-122017-001066-B | <1
WS- 001067 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C100 in bathroom |  |  | WF-12018-001067 | 2018-01-05 | FT-FY18-012018-001067-A | <1 | FT-FY18-012018-001067-B | <1
WS- 001068 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C108 in bathroom |  |  | WF-12018-001068 | 2018-01-05 | FT-FY18-012018-001068-A | <1 | FT-FY18-012018-001068-B | <1
WS- 001069 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C101 in bathroom |  |  | WF-12018-001069 | 2018-01-05 | FT-FY18-012018-001069-A | <1 | FT-FY18-012018-001069-B | <1
WS- 001070 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C107 in bathroom |  |  | WF-12018-001070 | 2018-01-05 | FT-FY18-012018-001070-A | <1 | FT-FY18-012018-001070-B | <1
WS- 001071 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C102 in bathroom |  |  | WF-12018-001071 | 2018-01-05 | FT-FY18-012018-001071-A | <1 | FT-FY18-012018-001071-B | <1
WS- 001072 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C106 in bathroom |  |  | WF-12018-001072 | 2018-01-05 | FT-FY18-012018-001072-A | <1 | FT-FY18-012018-001072-B | <1
WS- 001074 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C105 in bathroom |  |  | WF-12018-001074 | 2018-01-05 | FT-FY18-012018-001074-A | <1 | FT-FY18-012018-001074-B | <1
WS- 001075 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C104 in bathroom |  |  | WF-12018-001075 | 2018-01-05 | FT-FY18-012018-001075-A | <1 | FT-FY18-012018-001075-B | <1
WS- 009675 | 2017-05-17 | 2018-05-17 | Basement | Cooler | In multi-purpose room |  |  | WF-52017-009675 | 2018-01-05 | FT-FY18-052017-009675-A | <1 | FT-FY18-052017-009675-B | <1
WS- 001073 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C103 in bathroom |  |  | WF-12018-001073 | 2018-01-05 | FT-FY18-012018-001073-A | 14 | FT-FY18-012018-001073-B | 8.7

## Remediation (Plumbing Check)
RECORD ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location | WATER FILTERS Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001073 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C103 in bathroom | WF-12018-001073 | 2018-01-17 | FT-FY18-012018-001073-A | 12 | FT-FY18-012018-001073-B | 5

## Remediation (Device Replacement
RECORD ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location | WATER FILTERS Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001073 | 2018-01-02 | 2019-01-02 | Ground Floor | Bathroom | POD C, in classroom C103 in bathroom | WF-12018-001073 | 2018-01-23 | FT-FY18-012018-001073-A | 2 | FT-FY18-012018-001073-B | 1.9