## FY24 Filter Test
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001454 | 2023-05-08 | 2024-05-08 | Basement | Bottle Filler | In lobby adjacent to restrooms (bottle filler) |  | WF-05082023-001454 | 2023-11-01 | FT-FY24-09282023-001454-A | <1 | FT-FY24-09282023-001454-B | 1.9
WS- 001455 | 2023-05-08 | 2024-05-08 | 1 | Health Suite | In health suite | Mid | WF-05082023-001455 | 2023-11-01 | FT-FY24-09282023-001455-A | <1 | FT-FY24-09282023-001455-B | <1
WS- 001457 | 2023-05-08 | 2024-05-08 | Basement | Cooler | In lobby adjacent to restrooms |  | WF-05082023-001457 | 2023-11-01 | FT-FY24-09282023-001457-A | <1 | FT-FY24-09282023-001457-B | <1
WS- 001458 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 106 | Left | WF-08152023-001458 | 2023-11-01 | FT-FY24-09282023-001458-A | 2.8 | FT-FY24-09282023-001458-B | <1
WS- 001459 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 106 | Right | WF-05082023-001459 | 2023-11-01 | FT-FY24-09282023-001459-A | <1 | FT-FY24-09282023-001459-B | <1
WS- 001460 | 2023-05-08 | 2024-05-08 | 1 | Cooler | In hallway adjacent to room 104 |  | WF-05082023-001460 | 2023-11-01 | FT-FY24-09282023-001460-A | <1 | FT-FY24-09282023-001460-B | <1
WS- 001461 | 2023-05-08 | 2024-05-08 | 1 | Cooler | In hallway adjacent to room 103 |  | WF-05082023-001461 | 2023-11-01 | FT-FY24-09282023-001461-A | <1 | FT-FY24-09282023-001461-B | <1
WS- 001462 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 104 | Left | WF-08152023-001462 | 2023-11-01 | FT-FY24-09282023-001462-A | <1 | FT-FY24-09282023-001462-B | <1
WS- 001463 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 104 | Right | WF-05082023-001463 | 2023-11-01 | FT-FY24-09282023-001463-A | <1 | FT-FY24-09282023-001463-B | <1
WS- 001464 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 102 | Right | WF-08152023-001464 | 2023-11-01 | FT-FY24-09282023-001464-A | <1 | FT-FY24-09282023-001464-B | <1
WS- 001465 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 102 | Right | WF-05082023-001465 | 2023-11-01 | FT-FY24-09282023-001465-A | 1.0 | FT-FY24-09282023-001465-B | <1
WS- 001466 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 101 | Left | WF-08152023-001466 | 2023-11-01 | FT-FY24-09282023-001466-A | <1 | FT-FY24-09282023-001466-B | <1
WS- 001467 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 101 | Right | WF-05082023-001467 | 2023-11-01 | FT-FY24-09282023-001467-A | <1 | FT-FY24-09282023-001467-B | <1
WS- 001468 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 103 | Left | WF-08152023-001468 | 2023-11-01 | FT-FY24-09282023-001468-A | 2.7 | FT-FY24-09282023-001468-B | <1
WS- 001469 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 103 | Right | WF-05082023-001469 | 2023-11-01 | FT-FY24-09282023-001469-A | <1 | FT-FY24-09282023-001469-B | <1
WS- 001470 | 2023-08-15 | 2024-08-15 | 1 | Combo Faucet | In classroom 105 | Left | WF-08152023-001470 | 2023-11-01 | FT-FY24-09282023-001470-A | 1.2 | FT-FY24-09282023-001470-B | <1
WS- 001471 | 2023-05-08 | 2024-05-08 | 1 | Combo Fountain | In classroom 105 | Right | WF-05082023-001471 | 2023-11-01 | FT-FY24-09282023-001471-A | <1 | FT-FY24-09282023-001471-B | <1
WS- 001472 | 2023-05-08 | 2024-05-08 | 2 | Break Room | In staff lounge | Mid | WF-05082023-001472 | 2023-11-01 | FT-FY24-09282023-001472-A | <1 | FT-FY24-09282023-001472-B | <1
WS- 001473 | 2023-05-08 | 2024-05-08 | 2 | Cooler | In hallway across from janitor closet |  | WF-05082023-001473 | 2023-11-01 | FT-FY24-09282023-001473-A | <1 | FT-FY24-09282023-001473-B | <1
WS- 001474 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 208 | Left | WF-08152023-001474 | 2023-11-01 | FT-FY24-09282023-001474-A | 1.7 | FT-FY24-09282023-001474-B | <1
WS- 001475 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 208 | Right | WF-05082023-001475 | 2023-11-01 | FT-FY24-09282023-001475-A | <1 | FT-FY24-09282023-001475-B | <1
WS- 001476 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 212 | Left | WF-08152023-001476 | 2023-11-01 | FT-FY24-09282023-001476-A | 1.3 | FT-FY24-09282023-001476-B | <1
WS- 001477 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 212 | Right | WF-05082023-001477 | 2023-11-01 | FT-FY24-09282023-001477-A | <1 | FT-FY24-09282023-001477-B | <1
WS- 001478 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 211 | Left | WF-08152023-001478 | 2023-11-01 | FT-FY24-09282023-001478-A | 2.9 | FT-FY24-09282023-001478-B | <1
WS- 001479 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 211 | Right | WF-05082023-001479 | 2023-11-01 | FT-FY24-09282023-001479-A | <1 | FT-FY24-09282023-001479-B | <1
WS- 001480 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 207 | Left | WF-08152023-001480 | 2023-11-01 | FT-FY24-09282023-001480-A | 2.0 | FT-FY24-09282023-001480-B | <1
WS- 001481 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 207 | Right | WF-05082023-001481 | 2023-11-01 | FT-FY24-09282023-001481-A | <1 | FT-FY24-09282023-001481-B | <1
WS- 001482 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 210 | Left | WF-08152023-001482 | 2023-11-01 | FT-FY24-09282023-001482-A | 5.5 | FT-FY24-09282023-001482-B | <1
WS- 001483 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In Classroom 210 | Right | WF-05082023-001483 | 2023-11-01 | FT-FY24-09282023-001483-A | <1 | FT-FY24-09282023-001483-B | <1
WS- 001484 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 209 | Left | WF-08152023-001484 | 2023-11-01 | FT-FY24-09282023-001484-A | 5.8 | FT-FY24-09282023-001484-B | <1
WS- 001485 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In Classroom 209 | Right | WF-05082023-001485 | 2023-11-01 | FT-FY24-09282023-001485-A | <1 | FT-FY24-09282023-001485-B | <1
WS- 001486 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 206 | Left | WF-08152023-001486 | 2023-11-01 | FT-FY24-09282023-001486-A | 1.8 | FT-FY24-09282023-001486-B | <1
WS- 001488 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 206 | Right | WF-08152023-001488 | 2023-11-01 | FT-FY24-09282023-001488-A | <1 | FT-FY24-09282023-001488-B | <1
WS- 001490 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 205 |  | WF-08152023-001490 | 2023-11-01 | FT-FY24-09282023-001490-A | <1 | FT-FY24-09282023-001490-B | <1
WS- 001491 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 205 |  | WF-05082023-001491 | 2023-11-01 | FT-FY24-09282023-001491-A | <1 | FT-FY24-09282023-001491-B | <1
WS- 001492 | 2023-05-08 | 2024-05-08 | 2 | Cooler | In hallway adjacent to room 204 |  | WF-05082023-001492 | 2023-11-01 | FT-FY24-09282023-001492-A | <1 | FT-FY24-09282023-001492-B | <1
WS- 001493 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 203 | Left | WF-08152023-001493 | 2023-11-01 | FT-FY24-09282023-001493-A | <1 | FT-FY24-09282023-001493-B | <1
WS- 001494 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 203 | Right | WF-05082023-001494 | 2023-11-01 | FT-FY24-09282023-001494-A | <1 | FT-FY24-09282023-001494-B | <1
WS- 001495 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 204 | Left | WF-08152023-001495 | 2023-11-01 | FT-FY24-09282023-001495-A | <1 | FT-FY24-09282023-001495-B | <1
WS- 001496 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 204 | Right | WF-05082023-001496 | 2023-11-01 | FT-FY24-09282023-001496-A | <1 | FT-FY24-09282023-001496-B | <1
WS- 001497 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 201 | Left | WF-08152023-001497 | 2023-11-01 | FT-FY24-09282023-001497-A | 1.1 | FT-FY24-09282023-001497-B | <1
WS- 001498 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 201 | Right | WF-05082023-001498 | 2023-11-01 | FT-FY24-09282023-001498-A | <1 | FT-FY24-09282023-001498-B | <1
WS- 001499 | 2023-08-15 | 2024-08-15 | 2 | Combo Faucet | In classroom 202 | Left | WF-08152023-001499 | 2023-11-01 | FT-FY24-09282023-001499-A | <1 | FT-FY24-09282023-001499-B | <1
WS- 001500 | 2023-05-08 | 2024-05-08 | 2 | Combo Fountain | In classroom 202 | Right | WF-05082023-001500 | 2023-11-01 | FT-FY24-09282023-001500-A | <1 | FT-FY24-09282023-001500-B | <1
WS- 001503 | 2023-08-15 | 2024-08-15 | 1 | Bathroom | In classroom 101 in bathroom |  | WF-08152023-001503 | 2023-11-01 | FT-FY24-09282023-001503-A | <1 | FT-FY24-09282023-001503-B | <1
WS- 001504 | 2023-08-15 | 2024-08-15 | 1 | Bathroom | In classroom 102 in bathroom |  | WF-08152023-001504 | 2023-11-01 | FT-FY24-09282023-001504-A | <1 | FT-FY24-09282023-001504-B | <1
WS- 001505 | 2023-08-15 | 2024-08-15 | 1 | Bathroom | In classroom 103 in bathroom |  | WF-08152023-001505 | 2023-11-01 | FT-FY24-09282023-001505-A | <1 | FT-FY24-09282023-001505-B | <1
WS- 001506 | 2023-08-15 | 2024-08-15 | 1 | Bathroom | In classroom 104 in bathroom |  | WF-08152023-001506 | 2023-11-01 | FT-FY24-09282023-001506-A | <1 | FT-FY24-09282023-001506-B | <1
WS- 001508 | 2023-08-15 | 2024-08-15 | 1 | Bathroom | In classroom 106 in bathroom |  | WF-08152023-001508 | 2023-11-01 | FT-FY24-09282023-001508-A | <1 | FT-FY24-09282023-001508-B | <1

## Food Prep Sink
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001450 | 2022-12-28 | 2023-12-28 | Basement | Food Prep Sink | In kitchen second clockwise from entry door | Mid | WF-12282022-001450 | 2023-11-01 | FT-FY24-09282023-001450-A | 2.8 | FT-FY24-09282023-001450-B | 1.9

## Plumbing Check
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001482 | 2023-11-07 | 11/7/024 | 2 | Combo Faucet | In classroom 210 | Left | WF-11072023-001482 | 2023-11-14 | FT-FY24-1108023-001482-A | <1 | FT-FY24-11082023-001482-B | <1
WS- 001484 | 2023-11-07 | 2024-11-07 | 2 | Combo Faucet | In classroom 209 | Left | WF-11072023-001484 | 2023-11-14 | FT-FY24-11082023-001484-A | 9.5 | FT-FY24-11082023-001484-B | <1

## Device Replacement
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS- 001484 | 2023-11-17 | 2024-11-17 | 2 | Combo Faucet | In classroom 209 | Left | WF-11172023-001484 | 2023-11-27 | FT-FY24-11192023-001484-A | 3 | FT-FY24-11192023-001484-B | <1