## FY24 Filter Test
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location |  |  | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS-015350 | 2023-05-17 | 2024-05-17 | 1 | Bottle Filler | In hallway adjacent to 127 all gender restroom |  |  | WF-05172023-015350 | 2023-11-09 | FT-FY24-10102023-015350-A | 1.2 | FT-FY24-10102023-015350-B | <1
WS-015351 | 2023-05-17 | 2024-05-17 | 1 | Cooler | In hallway adjacent to 127 all gender restroom | High | Left | WF-05172023-015351 | 2023-11-09 | FT-FY24-10102023-015351-A | <1 | FT-FY24-10102023-015351-B | <1
WS-015352 | 2023-05-17 | 2024-05-17 | 1 | Cooler | In hallway adjacent to 127 all gender restroom | Low | Right | WF-05172023-015352 | 2023-11-09 | FT-FY24-10102023-015352-A | <1 | FT-FY24-10102023-015352-B | <1
WS-015353 | 2023-05-17 | 2024-05-17 | 1 | Health Suite | In room 130 inside health suite 131 |  |  | WF-05172023-015353 | 2023-11-09 | FT-FY24-10102023-015353-A | <1 | FT-FY24-10102023-015353-B | <1
WS-015360 | 2023-09-25 | 2024-09-25 | 1 | Combo Faucet | In room 100 infant |  | Left | WF-09252023-015360 | 2023-11-09 | FT-FY24-10102023-015360-A | <1 | FT-FY24-10102023-015360-B | <1
WS-015361 | 2023-05-17 | 2024-05-17 | 1 | Combo Fountain | In room 100 infant |  | Left | WF-05172023-015361 | 2023-11-09 | FT-FY24-10102023-015361-A | <1 | FT-FY24-10102023-015361-B | <1
WS-015362 | 2023-05-17 | 2024-05-17 | 1 | Combo Fountain | In room 100 infant |  | Right | WF-05172023-015362 | 2023-11-09 | FT-FY24-10102023-015362-A | <1 | FT-FY24-10102023-015362-B | <1
WS-015363 | 2023-09-25 | 2024-09-25 | 1 | Combo Faucet | In room 100 infant |  | Right | WF-09252023-015363 | 2023-11-09 | FT-FY24-10102023-015363-A | <1 | FT-FY24-10102023-015363-B | <1
WS-015364 | 2023-09-25 | 2024-09-25 | 1 | Classroom Faucet | In room 101 toddler room 1 |  |  | WF-09252023-015364 | 2023-11-09 | FT-FY24-10102023-015364-A | <1 | FT-FY24-10102023-015364-B | <1
WS-015365 | 2023-05-17 | 2024-05-17 | 1 | Combo Fountain | In room 101 toddler room 1 |  |  | WF-05172023-015365 | 2023-11-09 | FT-FY24-10102023-015365-A | <1 | FT-FY24-10102023-015365-B | <1
WS-015366 | 2023-09-25 | 2024-09-25 | 1 | Combo Faucet | In room 101 toddler room 1 |  |  | WF-09252023-015366 | 2023-11-09 | FT-FY24-10102023-015366-A | <1 | FT-FY24-10102023-015366-B | <1
WS-015367 | 2023-05-17 | 2024-05-17 | 1 | Break Room | In room 105 workroom |  |  | WF-05172023-015367 | 2023-11-09 | FT-FY24-10102023-015367-A | <1 | FT-FY24-10102023-015367-B | <1
WS-015368 | 2023-09-25 | 2024-09-25 | 2 | Combo Faucet | In room 215 pre-s/pre-k 4 |  |  | WF-09252023-015368 | 2023-11-09 | FT-FY24-10102023-015368-A | <1 | FT-FY24-10102023-015368-B | <1
WS-015370 | 2023-09-25 | 2024-09-25 | 2 | Combo Faucet | In room 218 pre-s/pre-k 5 |  |  | WF-09252023-015370 | 2023-11-09 | FT-FY24-10102023-015370-A | <1 | FT-FY24-10102023-015370-B | <1
WS-015372 | 2023-09-25 | 2024-09-25 | 2 | Combo Faucet | In room 200 toddler room 2 |  |  | WF-09252023-015372 | 2023-11-09 | FT-FY24-10102023-015372-A | <1 | FT-FY24-10102023-015372-B | <1
WS-015373 | 2023-05-17 | 2024-05-17 | 2 | Combo Fountain | In room 200 toddler room 2 |  |  | WF-05172023-015373 | 2023-11-09 | FT-FY24-10102023-015373-A | <1 | FT-FY24-10102023-015373-B | <1
WS-015374 | 2023-09-25 | 2024-09-25 | 2 | Classroom Faucet | In room 200 toddler room 2 |  |  | WF-09252023-015374 | 2023-11-09 | FT-FY24-10102023-015374-A | <1 | FT-FY24-10102023-015374-B | <1
WS-015375 | 2023-09-25 | 2024-09-25 | 2 | Classroom Faucet | In room 206 toddler room 3 |  |  | WF-09252023-015375 | 2023-11-09 | FT-FY24-10102023-015375-A | <1 | FT-FY24-10102023-015375-B | <1
WS-015376 | 2023-05-17 | 2024-05-17 | 2 | Combo Fountain | In room 206 toddler room 3 |  |  | WF-05172023-015376 | 2023-11-09 | FT-FY24-10102023-015376-A | <1 | FT-FY24-10102023-015376-B | <1
WS-015377 | 2023-09-25 | 2024-09-25 | 2 | Combo Faucet | In room 206 toddler room 3 |  |  | WF-09252023-015377 | 2023-11-09 | FT-FY24-10102023-015377-A | <1 | FT-FY24-10102023-015377-B | <1
WS-015378 | 2023-05-17 | 2024-05-17 | 2 | Bottle Filler | In hallway adjacent to room 212 |  |  | WF-05172023-015378 | 2023-11-09 | FT-FY24-10102023-015378-A | <1 | FT-FY24-10102023-015378-B | <1
WS-015379 | 2023-05-17 | 2024-05-17 | 2 | Cooler | In hallway adjacent to room 212 | High | Left | WF-05172023-015379 | 2023-11-09 | FT-FY24-10102023-015379-A | <1 | FT-FY24-10102023-015379-B | <1
WS-015380 | 2023-05-17 | 2024-05-17 | 2 | Cooler | In hallway adjacent to room 212 | Low | Right | WF-05172023-015380 | 2023-11-09 | FT-FY24-10102023-015380-A | <1 | FT-FY24-10102023-015380-B | <1
WS-015381 | 2023-09-25 | 2024-09-25 | 2 | Combo Faucet | In room 209 pre-s/pre-k 3 |  |  | WF-09252023-015381 | 2023-11-09 | FT-FY24-10102023-015381-A | <1 | FT-FY24-10102023-015381-B | <1
WS-015383 | 2023-09-25 | 2024-09-25 | 3 | Combo Faucet | In room 312 pre-s/pre-k 7 |  |  | WF-09252023-015383 | 2023-11-09 | FT-FY24-10102023-015383-A | <1 | FT-FY24-10102023-015383-B | <1
WS-015384 | 2023-05-17 | 2024-05-17 | 3 | Combo Fountain | In room 312 pre-s/pre-k 7 |  |  | WF-05172023-015384 | 2023-11-09 | FT-FY24-10102023-015384-A | <1 | FT-FY24-10102023-015384-B | <1
WS-015385 | 2023-09-25 | 2024-09-25 | 3 | Combo Faucet | In room 315 pre-s/pre-k 8 |  |  | WF-09252023-015385 | 2023-11-09 | FT-FY24-10102023-015385-A | <1 | FT-FY24-10102023-015385-B | <1
WS-015389 | 2023-09-25 | 2024-09-25 | 3 | Combo Faucet | In room 300 pre-s/pre-k 6 |  |  | WF-09252023-015389 | 2023-11-09 | FT-FY24-10102023-015389-A | <1 | FT-FY24-10102023-015389-B | <1
WS-015392 | 2023-05-17 | 2024-05-17 | 3 | Combo Fountain | In room 304 music |  |  | WF-05172023-015392 | 2023-11-09 | FT-FY24-10102023-015392-A | <1 | FT-FY24-10102023-015392-B | <1
WS-015393 | 2023-05-17 | 2024-05-17 | 3 | Bottle Filler | In hallway adjacent to room 304 |  |  | WF-05172023-015393 | 2023-11-09 | FT-FY24-10102023-015393-A | <1 | FT-FY24-10102023-015393-B | <1
WS-015394 | 2023-05-17 | 2024-05-17 | 3 | Cooler | In hallway adjacent to room 304 | High | Left | WF-05172023-015394 | 2023-11-09 | FT-FY24-10102023-015394-A | <1 | FT-FY24-10102023-015394-B | <1
WS-015395 | 2023-05-17 | 2024-05-17 | 3 | Cooler | In hallway adjacent to room 304 | Low | Right | WF-05172023-015395 | 2023-11-09 | FT-FY24-10102023-015395-A | <1 | FT-FY24-10102023-015395-B | <1
WS-015397 | 2023-05-17 | 2024-05-17 | 3 | Combo Fountain | In room 308 art lab |  |  | WF-05172023-015397 | 2023-11-09 | FT-FY24-10102023-015397-A | <1 | FT-FY24-10102023-015397-B | <1
WS-015399 | 2023-09-25 | 2024-09-25 | 4 | Combo Faucet | In room 413 pre-s/pre-k 9 |  |  | WF-09252023-015399 | 2023-11-09 | FT-FY24-10102023-015399-A | <1 | FT-FY24-10102023-015399-B | <1
WS-015405 | 2023-05-17 | 2024-05-17 | 4 | Break Room | In break room area across from room 404 |  |  | WF-05172023-015405 | 2023-11-09 | FT-FY24-10102023-015405-A | <1 | FT-FY24-10102023-015405-B | <1
WS-015406 | 2023-05-17 | 2024-05-17 | 4 | Break Room | In room 403 lactation |  |  | WF-05172023-015406 | 2023-11-09 | FT-FY24-10102023-015406-A | <1 | FT-FY24-10102023-015406-B | <1
WS-015407 | 2023-05-17 | 2024-05-17 | 4 | Bottle Filler | In hallway adjacent to room 410 |  |  | WF-05172023-015407 | 2023-11-09 | FT-FY24-10102023-015407-A | <1 | FT-FY24-10102023-015407-B | <1
WS-015408 | 2023-05-17 | 2024-05-17 | 4 | Cooler | In hallway adjacent to room 410 | High | Left | WF-05172023-015408 | 2023-11-09 | FT-FY24-10102023-015408-A | <1 | FT-FY24-10102023-015408-B | <1
WS-015409 | 2023-05-17 | 2024-05-17 | 4 | Cooler | In hallway adjacent to room 410 | Low | Right | WF-05172023-015409 | 2023-11-09 | FT-FY24-10102023-015409-A | <1 | FT-FY24-10102023-015409-B | <1
WS-015411 | 2023-09-25 | 2024-09-25 | 2 | Bathroom | In bathroom of room 206 |  |  | WF-09252023-015411 | 2023-11-09 | FT-FY24-10102023-015411-A | <1 | FT-FY24-10102023-015411-B | <1

## Food Prep Sink
Record ID | Filter Installed Date | Filter Expiration Date | Floor | Device Type | Device Location | Water Filter's Name | Date Analyzed | 1st Draw - Sample ID | FT Final Result - 1st Draw (ppb) | 2nd Draw - Sample ID | FT Final Result - 2nd Draw (ppb)
WS-015358 | 2023-01-25 | 2024-01-25 | 1 | Food Prep Sink | In kitchen fifth clockwise from entry | WF-01252023-015358 | 2023-11-09 | FT-FY24-10102023-015358-A | <1 | FT-FY24-10102023-015358-B | <1